## Page 1
Control Number |  | Attch. | Section/Drawing |  | Step/Note |  | Ref. Doc. | Comment/Issue |  | Recommendation / Resolution |  | Reviewer |  | Reviewer Org |  | Date Opened |  | Date Closed | Status |  | Closed By | AE Response | Notes | Org Response
1 |  |  | 260533 |  | 3.4.E |  |  | Section 260533, Section 3.4.E: What penetration seals will be used? |  | Include detail of penetration seals. |  | Jisun Lee, CEO |  |  |  | 4/4/2013 |  |  | CLOSING
2 |  |  | 260533 |  | 1.3.E |  |  | Please explain Section 260533, 1.3.E. |  |  |  | Edward Swain, Head Reviewer |  | 34342 |  | 4/4/2013 |  |  | OPEN
3 |  |  | 260533 |  | 2.1.B.3 |  |  | Section 260533, 2.1.B.3: What type(s) of locknut will be used? |  |  |  | Jisun Lee, CEO |  |  |  | 4/4/2013 |  |  | OPEN
4 |  |  | 260533 |  |  |  |  | Section 260533: How have interaction of different metal alloys (ferrous alloy FD, Stainless Steel, galvanized steel, etc.) been considered for Galvanic Corrosion? |  |  |  | Jisun Lee, CEO |  |  |  | 4/4/2013 |  |  | OPEN
5 |  |  | 260533 |  |  |  |  | Section 260533: The zinc coating thickness should be specified, or else be done to NEMA 250 (or other applicable standard). |  |  |  | Edward Swain, Head Reviewer |  | 34342 |  | 4/4/2013 |  |  | OPEN
6 |  |  | 260533 |  |  |  |  | Section 260533: Enclosures in those interior enviroments that are not regularly wet should be NEMA 250 Type 5 to additionally protect against settling dust and drips or light leaks such as rain occasionally leaking through the ceiling (not covered by Type 1). |  |  |  | Edward Swain, Head Reviewer |  | 34342 |  | 4/4/2013 |  |  | OPEN
7 |  |  | 260533 |  |  |  |  | All Seismic Sections: Manufacturer's certification should also indicate the extent (in G's, pounds-force, Shock Response Spectrum, or other suitable method) of the seismic force that the respective unit can withstand in the vertical and horizontal directions. If seismic analysis is done by computer modelling or calculation instead of testing, the manufacture should indicate the computer program used, waveform input, and his/her engineering assumptions. If seismic analysis is done by test, then the manufacture should describe the test method and setup and comparison of the test environment to the actual operation ("real world") environment. |  |  |  | Edward Swain, Head Reviewer |  | 34342 |  | 4/4/2013 |  |  | OPEN
8 |  |  |  | 260529 |  |  |  |  | Section 260529: What grade(s) of Stainless Steel? Since all hardware is to be galvanized and all exterior hardware to be hot-dip galvanized (2.3.A.2), would that include hot-dip galvanized Stainless Steel for the exterior mechanical anchors (2.2.I)? How have the difficulties of hot-dip galvanizing Stainless Steel been addressed? How have interaction of different metal alloys been considered for Galvanic Corrosion especially in exterior environments? |  |  |  | Edward Swain, Head Reviewer |  | 34342 |  | 4/4/2013 |  |  | OPEN
9 |  |  |  | HVAC Recommendations |  |  |  |  | Document needs to cite the specific ASHRAE Standards instead of just referring to ASHRAE in general. |  | N/A. Negligible Difference |  | Jisun Lee, CEO |  |  |  | 4/4/2013 |  |  | CLOSING
10 |  |  |  | HVAC Recommendations |  |  |  |  | Various grammatical errors: "sealed up" instead of "sealed" (redundancy), "see….below" instead of "see … below this paragraph" (dangling prepositions), etc. |  | Fix errors. |  | Jisun Lee, CEO |  |  |  | 4/4/2013 |  |  | CLOSING |  |  |  |  | Drawing was updated.
11 | 011.pdf |  |  | 260533 |  | 1.3.E |  |  | Please explain Section 260533, 1.3.E. Is this related to attached schematic? |  |  |  | Jisun Lee, CEO |  |  |  | 4/4/2013 |  |  | OPEN